## Sheet1
Plant | name | token | Building | Area | Location | Make | Model | isMktCalculationEnabled | Enable_Humid_NLT | Enable_Temp_NLT | Enable_Humid_NMT | Enable_Temp_NMT | label | type | Low Temperature Range | High Temperature Range | Low Humidity Range | High Humidity Range | Low Temperature Limit | High Temperature Limit | Low Humidity Limit | High Humidity Limit | temp_decimals | humid_decimals
Gagillapur | CWH/RDU/001-00 | IOTGW01_163 | CWH Block | Stability | IT Server Room | Global | CR120 | FALSE | FALSE | TRUE | FALSE | TRUE | IOTGW01_163 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 18 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/002-01 | IOTGW03_121 | CWH Block | QC 3 | LCMS Room-II | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_121 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/003-00 | IOTGW03_119 | CWH Block | QC 3 | Working standard & reference Standard storage Room (or) stability Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_119 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/004-00 | IOTGW03_127 | CWH Block | QC 3 | Sieve Analyzer & BD Apparatus Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_127 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/005-00 | IOTGW03_124 | CWH Block | QC 3 | KF & Auto titrator Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_124 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 30 | 1 | 0
Gagillapur | CWH/RDU/006-00 | IOTGW03_122 | CWH Block | QC 3 | Dissolution & UV Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_122 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/007-00 | IOTGW03_125 | CWH Block | QC 3 | Malvern/AAS Instrument Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_125 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/008-00 | IOTGW03_126 | CWH Block | QC 3 | GC/GCMS Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_126 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/009-00 | IOTGW03_123 | CWH Block | QC 3 | Wet Lab | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_123 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/010-00 | IOTGW03_118 | CWH Block | QC 3 | Sample Preparation Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_118 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/011-00 | IOTGW03_117 | CWH Block | QC 3 | HPLC Room | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_117 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/012-00 | IOTGW03_120 | CWH Block | QC 3 | LCMS Room-I | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_120 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/013-00 | IOTGW04_141 | CWH Block | QC | Sample Storage Room | Global | CR131 | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_141 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/014-00 | IOTGW04_131 | CWH Block | QC | GC Room (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_131 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/015-00 | IOTGW04_137 | CWH Block | QC | Hot Zone (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_137 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/016-00 | IOTGW04_135 | CWH Block | QC | Weighing Room (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_135 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/017-00 | IOTGW04_134 | CWH Block | QC | Chamber room (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_134 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/018-00 | IOTGW04_133 | CWH Block | QC | Sieving& Sample destruction chamber room(QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_133 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/019-00 | IOTGW04_138 | CWH Block | QC | Instrumentation room-1 (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_138 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/020-00 | IOTGW04_140 | CWH Block | QC | HPLC Room (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_140 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/021-00 | IOTGW04_139 | CWH Block | QC | Dissolution Room (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_139 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/022-00 | IOTGW04_136 | CWH Block | QC | Wet lab (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_136 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/023-00 | IOTGW04_132 | CWH Block | QC | Sample Preparation area (QC) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_132 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/024-00 | IOTGW04_130 | CWH Block | QC | QC-II (Dissolution lab-II) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_130 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/025-00 | IOTGW01_161 | CWH Block | Stability | Chambers Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_161 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/026-00 | IOTGW03_116 | CWH Block | QC 3 | Sample Receipt & Sample Storage Room | Global | CR131 | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_116 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/027-00 | IOTGW03_129 | CWH Block | Stability | control and retention Sample room Rack No:U35(H.S) | Global | CR131 | FALSE | FALSE | TRUE | TRUE | TRUE | IOTGW03_129 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 20 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/028-00 | IOTGW03_128 | CWH Block | Stability | control and retention Sample room Rack No:W1(C.S) | Global | CR131 | FALSE | FALSE | TRUE | TRUE | TRUE | IOTGW03_128 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 20 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/029-00 | IOTGW01_180 | CWH Block | Module-E | Excipient Dispensing Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_180 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/030-00 | IOTGW01_182 | CWH Block | Module-E | API Dispensing Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_182 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/031-00 | IOTGW01_186 | CWH Block | Module-E | Blender Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_186 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/032-00 | IOTGW01_184 | CWH Block | Module-E | Granulation Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_184 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/033-00 | IOTGW01_111 | CWH Block | Module-F(AHU-044) | API Dispensing Booth Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_111 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/034-00 | IOTGW01_113 | CWH Block | Module-F(AHU-045) | Excipient Dispensing Booth Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_113 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/035-00 | IOTGW01_108 | CWH Block | Module-F(AHU-046) | Sifting Holding Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_108 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/036-00 | IOTGW01_106 | CWH Block | Module-F(AHU-046) | Binder Charging Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_106 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/037-00 | IOTGW01_110 | CWH Block | Module-F(AHU-046) | Charging Area( Near RMG & FBP Area) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_110 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/038-00 | IOTGW01_105 | CWH Block | Module-F(AHU-046) | Binder preparation Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_105 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/039-00 | IOTGW01_104 | CWH Block | Module-F(AHU-046,AHU-047) | Granulation Area(Near Office Room) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_104 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/040-00 | IOTGW01_103 | CWH Block | Module-F(AHU-048) | Blender Area-01 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_103 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/041-00 | IOTGW01_107 | CWH Block | Module-F(AHU-048) | Blender Charging Area-01 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_107 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/042-00 | IOTGW01_102 | CWH Block | Module-F(AHU-049) | Hold Area-01 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_102 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/043-00 | IOTGW01_109 | CWH Block | Module-F(AHU-050) | Blender Charging Area-02 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_109 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/044-00 | IOTGW01_101 | CWH Block | Module-F(AHU-050) | Blender Area-02 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_101 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/045-00 | IOTGW04_145 | CWH Block | QC Microbiology | LAF-1(Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_145 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/046-00 | IOTGW04_146 | CWH Block | QC Microbiology | LAF-2(Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_146 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/047-00 | IOTGW04_147 | CWH Block | QC Microbiology | BSC Room (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_147 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/048-00 | IOTGW04_142 | CWH Block | QC Microbiology | Water wet analysis Room (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_142 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/049-00 | IOTGW04_148 | CWH Block | QC Microbiology | Media Preparation Room (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_148 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/050-00 | IOTGW04_143 | CWH Block | QC Microbiology | General Lab (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_143 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/051-00 | IOTGW04_144 | CWH Block | QC Microbiology | Incubator room (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_144 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/052-00 | IOTGW04_149 | CWH Block | QC Microbiology | Media Storage room (Microbiology) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_149 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/053-00 | IOTGW01_177 | CWH Block | Stability | Sampling Booth-IV (GCW/WH/093) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_177 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/054-00 | IOTGW01_176 | CWH Block | Stability | Sampling Booth-III (GCW/WH/092) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_176 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/055-00 | IOTGW08_175 | CWH Block | Ware House | Module-F Warehouse Staging area (Hot spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_175 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/056-00 | IOTGW01_112 | CWH Block | Module-F | API Dispensing Material Entry Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_112 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/057-00 | IOTGW01_114 | CWH Block | Module-F | Excipient Dispensing Material Entry Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_114 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/058-00 | IOTGW01_115 | CWH Block | Module-F | Staging Area (Near lift 1st Floor) | Radix | HAWKEYE | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW01_115 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/059-00 | IOTGW01_183 | CWH Block | Module-E | API Staging Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_183 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/060-00 | IOTGW01_181 | CWH Block | Module-E | Excipient Staging Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_181 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/061-00 | IOTGW01_185 | CWH Block | Module-E | Shifter Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_185 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/062-00 | IOTGW08_169 | CWH Block | Ware House | Module-E staging area (HOT Sopt) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_169 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/063-00 | IOTGW03_34 | CWH Block | Ware House | Module-E staging area (Cold Sopt) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW03_34 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/064-00 | IOTGW08_164 | CWH Block | Ware House | Central warehouse FG(Cold Spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_164 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/065-00 | IOTGW08_165 | CWH Block | Ware House | Central warehouse FG (Hot Spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_165 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/066-00 | IOTGW08_172 | CWH Block | Ware House | Module-F RM Warehouse (Cold spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_172 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/067-00 | IOTGW08_173 | CWH Block | Ware House | Module-F RM Warehouse (Hot spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_173 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/068-00 | IOTGW08_174 | CWH Block | Ware House | Module-F Warehouse Staging area (Cold spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_174 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/069-00 | IOTGW08_166 | CWH Block | Ware House | Central warehouse RM (Cold Spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_166 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/070-00 | IOTGW08_167 | CWH Block | Ware House | Central warehouse RM (Hot Spot) | Radix | HAWKEYE RTC | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_167 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/071-00 | IOTGW08_178 | CWH Block | Module-F | 1.6KL Blender | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_178 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/072-00 | IOTGW01_179 | CWH Block | Module-F | 3.5KL Blender | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_179 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/073-01 | IOTGW01_170 | CWH Block | Stability | Sampling Booth(GCW/WH/001) | Global | CR120 | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_170 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/074-01 | IOTGW01_171 | CWH Block | Stability | Sampling Booth(GCW/WH/007) | Global | CR120 | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_171 | Temp_RH Sensor | -40 | 60 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/075-00 | IOTGW03_160 | CWH Block | Stability | Bottle Packing-IV (Bottle Unscrambler-4) | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_160 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/076-00 | IOTGW03_158 | CWH Block | Stability | Bottle Packing-IV Secondary Packing | Styrax | CPS1052CT | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW03_158 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/077-01 | IOTGW03_157 | CWH Block | Stability | Bottle Packing-IV(PM/WIP Area) | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_157 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/078-00 | IOTGW03_152 | CWH Block | Stability | Hold Area 4 th floor | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_152 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/079-00 | IOTGW03_150 | CWH Block | Stability | PM Store 4th Floor | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_150 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/080-00 | IOTGW03_153 | CWH Block | Stability | Blister packing-6 Primary Area | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_153 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/081-00 | IOTGW03_151 | CWH Block | Stability | Blister packing-6 Secondary Area | Styrax | CPS1052CT | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW03_151 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/082-00 | IOTGW03_154 | CWH Block | Stability | Bottle Packing-5 Primary packing | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_154 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/083-00 | IOTGW03_155 | CWH Block | Stability | Bottle Packing-5 Un scramble Area | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_155 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/085-00 | IOTGW03_159 | CWH Block | Stability | Bottle Packing-IV (Primary Area) | Styrax | CPS1052CT | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW03_159 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/086-00 | IOTGW04_187 | CWH Block | Stability | Control sample Hot Spot (TTD/QC/CSR Block) | Radix | HAWKEYE RTC | FALSE | FALSE | TRUE | TRUE | TRUE | IOTGW04_187 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 20 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/087-00 | IOTGW04_188 | CWH Block | Stability | Control sample Cold Spot (TTD/QC/CSR Block) | Radix | HAWKEYE | FALSE | FALSE | TRUE | TRUE | TRUE | IOTGW04_188 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 20 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/088-00 | IOTGW01_162 | CWH Block | Stability | Sample Storage Room | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_162 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/089-00 | IOTGW04_189 | CWH Block | Stability | Stability Chamber Area (TTD/QC/CSR Block) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW04_189 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 70 | 1 | 0
Gagillapur | CWH/RDU/090-00 | IOTGW01_190 | CWH Block | Module-E | Air Lock-02 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW01_190 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/091-00 | IOTGW08_198 | CWH Block | Stability | WIP Area (CWH 4th Floor) | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_198 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 25 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/092-00 | IOTGW08_196 | CWH Block | Stability | Blister Packing-3 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_196 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/093-00 | IOTGW08_201 | CWH Block | Stability | Secondary Packing (CWH 4th Floor) | Radix | HAWKEYE | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_201 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/094-00 | IOTGW08_194 | CWH Block | Stability | Blister Packing-5 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_194 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/095-00 | IOTGW08_200 | CWH Block | Stability | Blister Packing-07 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_200 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/096-00 | IOTGW08_193 | CWH Block | Stability | Liquid Mfg. and filling Area | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_193 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/097-00 | IOTGW08_192 | CWH Block | Stability | Secondary Packing (Liquid Mfg. and filling Area) | Radix | HAWKEYE | FALSE | FALSE | FALSE | FALSE | TRUE | IOTGW08_192 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 0 | 1 | 0
Gagillapur | CWH/RDU/098-00 | IOTGW08_191 | CWH Block | Stability | Inspection-3 / Bulk Packing / WIP | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_191 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/099-00 | IOTGW08_195 | CWH Block | Stability | CWH 4th Floor Blister Packing -04 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_195 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/100-00 | IOTGW08_199 | CWH Block | Stability | CWH 4th Floor Change Parts Room | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_199 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0
Gagillapur | CWH/RDU/101-00 | IOTGW08_197 | CWH Block | Stability | CWH Blister Packing -02 | Radix | HAWKEYE | FALSE | FALSE | FALSE | TRUE | TRUE | IOTGW08_197 | Temp_RH Sensor | 0 | 50 | 0 | 100 | 0 | 27 | 0 | 60 | 1 | 0